## Read me
AVSA OT/ICS Security Risk Assessment
IEC 62443-3-2 · fictional scenario for portfolio demonstration · no real client data
Organization | Aguas de Valdenor, S.A. (AVSA), fictional municipal water utility in northern Spain
Facility | ETAP Río Almora drinking-water treatment plant + distribution telemetry
Standard | IEC 62443-3-2 (risk assessment); refs NIST SP 800-82r3, MITRE ATT&CK for ICS
Assessment type | Architecture- and interview-based (paper assessment); no active scanning performed
Tabs in this workbook
Scoring Rubric | Consequence, likelihood, risk-band and security-level definitions used throughout
Zone & Conduit Register | ZCR 3. Target zones and conduits with SL-T, current SL-A, and gap
Risk Register | ZCR 4. 14 scored risks with inherent/residual ratings and ATT&CK for ICS refs
SL-T Summary | Target vs estimated-current security level per zone, with foundational-requirement notes
How to read risk scores | Risk = Likelihood × Consequence (1–25). Low 1–5 · Medium 6–10 · High 11–15 · Critical 16–25
Current network reality | The zone model is the TARGET. AVSA's network is currently flat/unsegmented (finding AO-2),
so these boundaries are not enforced today. The SL-T vs SL-A gap quantifies that security debt.
Disclaimer | Fictional organization; public frameworks only; no client data, proprietary material, or confidential artifacts.

## Scoring Rubric
Scoring Rubric
Applied consistently across the zone/conduit and risk registers
Consequence (rate the highest applicable dimension: public health / service continuity / personnel safety / environmental / regulatory-financial)
Rating | Descriptor | Water-utility anchor
1 | Negligible | No measurable effect on water quality, supply, or safety; trivial operational noise.
2 | Minor | Short, localized operational disruption; no customer supply loss; no health or safety impact.
3 | Moderate | Localized supply interruption (some customers, hours) or degraded control, recoverable within a shift; minor regulatory notification.
4 | Major | Wider/extended supply interruption, or loss of control/view; water-quality deviation caught before harm; NIS2-reportable; safety near-miss.
5 | Severe | Unsafe water reaches consumers, OR chlorine-gas release harms personnel, OR prolonged population-wide loss of supply; potential loss of life.
Likelihood (threat capability & motivation × exposure × effectiveness of existing controls; assessed inherent then residual)
Rating | Descriptor
1 | Rare: requires exceptional resources or access; strongly mitigated; no known targeting.
2 | Unlikely: requires significant capability or insider access; meaningful barriers present.
3 | Possible: achievable by a moderately capable actor; exposure exists; controls partial or weak.
4 | Likely: achievable with known techniques by a common actor; clear exposure; little/no effective control.
5 | Almost certain: trivial to exploit; actively targeted in the wild; exposed with no barrier.
Risk = Likelihood × Consequence (1–25)
Band | Score | Action
Low | 1–5 | Tolerable; monitor.
Medium | 6–10 | Treat within normal planning cycles.
High | 11–15 | Prioritized treatment required.
Critical | 16–25 | Urgent; treat ahead of routine work.
Security Level (SL): graded 1 to 4 by the attacker capability a zone must withstand
SL | Withstands
1 | Casual or coincidental violation (no real attacker).
2 | Intentional, simple means, low resources, generic skills, low motivation (common cybercriminal).
3 | Sophisticated means, moderate resources, ICS-specific skills, moderate motivation (capable OT-aware actor).
4 | Sophisticated means, extended resources, ICS-specific skills, high motivation (well-resourced nation-state).
SL-T = target (assigned by risk) · SL-A = achieved (actual today) · SL-C = capability (what a product can provide).

## Zone & Conduit Register
Zone & Conduit Register (ZCR 3)
Target zone model, grouped by consequence and function. Current network is flat (AO-2); gaps quantify the debt.
Zone | Name | Purdue | Key assets | Consequence driver | SL-T | Est. SL-A | Gap
Z1 | Enterprise | L4–5 | Corporate IT: billing, ERP, GIS, email, reporting server | External to SuC; modelled as a threat source (ransomware origin, Nov 2025) | n/a | n/a | n/a
Z2 | OT DMZ | L3.5 | TARGET: replica historian, MFA jump host, patch/AV staging. Does not exist today (AO-1). | Keystone IT/OT boundary; its absence is the single largest structural risk | 3 | 0 | 3
Z3 | Site Operations | L3 | Process historian, engineering workstation, field laptop | Historian bridges IT/OT (AO-1); EWS holds PLC-programming authority (AO-5) | 2 | 1 | 1
Z4 | Supervisory Control | L2 | Redundant SCADA pair, 4 operator WS, 6 HMIs (2× Windows 7) | Central control leverage over every downstream process; loss of view/control | 3 | 1 | 2
Z5 | Process Control | L1 | PA-1/2/3/5 PLCs (20 × S7-1500) + Level 0 field devices | Disruption of intake, coagulation, filtration, or high-lift; supply continuity | 2 | 1 | 1
Z6 | Chlorine Dosing Control | L1 | PA-4 PLCs (4 × S7-1500) + Level 0. Hardwired safety layer is separate/out-of-band. | PUBLIC HEALTH: dosing manipulation affects water safety. Highest-consequence zone. | 3 | 1 | 2
Z7 | Distribution Telemetry | L1 rem. | 13 × RTU/S7-1200 at 9 pumping stations + 4 reservoirs | Remote/unmanned, cellular; reservoir re-dosing RTUs carry a water-quality consequence | 2 (re-dosing: 3) | 0–1 | 2–3
Conduits
Conduit | Between | Purpose | Current state | SL-T
C1 | Z1 Enterprise ↔ Z2 OT DMZ | The IT/OT boundary; all cross-domain traffic | No DMZ exists; historian's 2nd NIC bypasses the firewall entirely (AO-1) | 3
C2 | Z2 OT DMZ ↔ Z3 Site Operations | Brokered replication, staged patches, jump-host access | Absent (no DMZ to broker through) | 3
C3 | Z3 Site Operations ↔ Z4 Supervisory | Historian data collection, engineering access | Same flat segment; unsegmented (AO-2) | 2
C4 | Z4 Supervisory ↔ Z5 Process Control | SCADA/HMI supervision and control (Profinet/OPC UA) | Flat; no conduit enforcement | 2
C5 | Z4 Supervisory ↔ Z6 Chlorine Dosing | Dosing supervision and setpoint commands | Flat; no enforced separation around the highest-consequence zone | 3
C6 | Z7 Telemetry ↔ plant (4G VPN) | Remote monitoring/control of distribution sites | VPN encrypted, but terminates directly inside the flat plant LAN (AO-2) | 3
C7 | Vendor remote access (Nortec) ↔ plant | SCADA support and PLC logic maintenance | Shared VPN account, standing access, no MFA (AO-3) | 3

## Risk Register
Risk Register (ZCR 4)
Risk = Likelihood × Consequence. Inherent = before existing controls; Residual = after. Cross-refs to AO-1…AO-5 and ATT&CK for ICS.
ID | Threat event | Zone/Conduit | Vuln | Threat source | C | L(i) | Inherent | Existing / compensating controls | L(r) | Residual | SL-T | ATT&CK for ICS
R-01 | Corporate ransomware pivots into the plant via the dual-homed historian | C1 / Z3 | AO-1 | Cybercriminal (ransomware) | 4 | 4 | 16 | IT firewall exists but the historian's 2nd NIC bypasses it; 24/7 ops may notice disruption | 3 | 12 | 3 | T0866 Exploitation of Remote Services; T0826 Loss of Availability
R-02 | Compromise of the cellular VPN or a remote RTU enables lateral movement into the flat plant LAN | C6 / Z4 | AO-2 | Cybercriminal / hacktivist | 4 | 3 | 12 | VPN is encrypted, but it terminates inside an unsegmented LAN, so no lateral containment | 3 | 12 | 3 | T0822 External Remote Services; T0886 Remote Services
R-03 | Theft or misuse of the shared Nortec VPN credential grants direct SCADA/PLC access | C7 / Z4 | AO-3 | Cybercriminal / malicious insider | 4 | 4 | 16 | None effective. Shared account, standing access, no MFA. | 3 | 12 | 3 | T0822 External Remote Services; T0859 Valid Accounts
R-04 | Manipulation of chlorine dosing setpoints degrades water quality reaching consumers | Z6 | Z6 + control access | Nation-state / capable ICS actor | 5 | 3 | 15 | Hardwired safety covers GAS RELEASE, not dosing setpoints; lab sampling may detect after the fact | 2 | 10 | 3 | T0836 Modify Parameter; T0831 Manipulation of Control
R-05 | Exploitation of a Windows 7 HMI provides a foothold in the supervisory zone | Z4 | AO-4 | Cybercriminal | 3 | 4 | 12 | Panels have some physical isolation, but sit on the flat LAN; OS unpatchable pending vendor requalification | 3 | 9 | 3 | T0866 Exploitation of Remote Services
R-06 | Phishing of the engineering-workstation user leads to an unauthorized PLC logic change | Z3 → Z5 | AO-5 | Cybercriminal / nation-state | 4 | 3 | 12 | None. EWS is dual-used for email/web with no application control. | 3 | 12 | 2 | T0865 Spearphishing Attachment; T0843 Program Download; T0821 Modify Controller Tasking
R-07 | Access to a remote RTU via default credentials manipulates pumping or reservoir re-dosing | Z7 | W-09 | Opportunistic / hacktivist | 4 | 4 | 16 | Physical locks vary by site; reservoir re-dosing carries a water-quality consequence | 3 | 12 | 3 | T0812 Default Credentials
R-08 | Unmanaged USB used for logic updates introduces malware into the OT environment | Z4 / Z5 | W-10 | Cybercriminal (incl. supply chain) | 4 | 3 | 12 | No USB control, allow-listing, or scanning of transient media | 3 | 12 | 2 | T0847 Replication Through Removable Media; T0864 Transient Cyber Asset
R-09 | Loss or failure of the field laptop holding the sole PLC logic backups extends incident recovery | Z5 | W-07 | Non-adversarial / theft | 3 | 3 | 9 | No centralized backup; single copy held on a portable device | 3 | 9 | n/a (RA) | supports recovery from T0809 Data Destruction
R-10 | Absence of an OT-specific incident response plan prolongs and worsens any incident | SuC-wide | W-08 | Amplifier (all actors) | 4 | 4 | 16 | IT IR plan excludes the plant; 24/7 staffing aids detection only, not response | 3 | 12 | n/a (TRE) | degrades response to Inhibit Response Function techniques
R-11 | Physical access to an unmanned distribution site enables local RTU compromise | Z7 | Z7 exposure / W-09 | Opportunistic / insider | 3 | 3 | 9 | Site locks present; consequence is localized to one station/reservoir | 2 | 6 | 2 | T0864 Transient Cyber Asset; T0812 Default Credentials
R-12 | The flat network lets a single foothold reach every OT asset (no restricted data flow) | SuC-wide | AO-2 | Amplifier (any actor) | 4 | 4 | 16 | None. No segmentation between Levels 2/3 or around external entry points. | 3 | 12 | 3 (RDF) | T0886 Remote Services (systemic amplifier)
R-13 | Ransomware or DoS on the SCADA pair causes loss of view and control for operators | Z4 | AO-1 / AO-2 | Cybercriminal | 4 | 3 | 12 | Redundant pair, but both nodes share the subnet and the same malware exposure | 3 | 12 | 3 | T0814 Denial of Service; T0815 Denial of View; T0813 Denial of Control
R-14 | Alarm suppression or spoofed readings mask an ongoing process manipulation | Z6 / Z4 | Z6 integrity | Nation-state / capable | 5 | 2 | 10 | Operator vigilance only; no command/telemetry integrity monitoring | 2 | 10 | 3 | T0878 Alarm Suppression; T0856 Spoof Reporting Message; T0838 Modify Alarm Settings

## SL-T Summary
Security Level Summary: Target vs Current
The SL-T minus SL-A gap is the security debt the remediation roadmap closes.
Zone | Name | SL-T (target) | Est. SL-A (current) | Gap | Notes
Z2 | OT DMZ | 3 | 0 | 3 | Zone absent entirely (AO-1). Largest single gap; top roadmap priority.
Z3 | Site Operations | 2 | 1 | 1 | Historian dual-homing and EWS dual-use drive the gap.
Z4 | Supervisory Control | 3 | 1 | 2 | Central control leverage; Windows 7 HMIs cap achievable SL-A.
Z5 | Process Control | 2 | 1 | 1 | Flat network is the main shortfall; endpoints otherwise modern.
Z6 | Chlorine Dosing Control | 3 | 1 | 2 | Highest consequence. FR vector: {IAC3,UC3,SI3,DC1,RDF3,TRE2,RA3}. DC only 1: setpoints are not confidential.
Z7 | Distribution Telemetry | 2 (re-dosing: 3) | 0–1 | 2–3 | Default creds (W-09) + cellular exposure. Reservoir re-dosing RTUs warrant SL-T 3.
SL 4 note: reserved for catastrophic consequence vs a determined nation-state; judged impractical/disproportionate for a municipal utility this size. SL 3 is the pragmatic ceiling.